## Slide 1
Organized by:
National Reconstruction Authority(NRA)
MOUD/District Project Implementation Unit (DLPIU)
Housing Recovery and Reconstruction Platform-Nepal (HRRP)
Housing Recovery and Reconstruction Platform-Nepal (HRRP) Orientation Program for Partner organizations
on
Confined Masonry Construction

## Slide 2: Why Confined Masonry ?
Poor performance of unreinforced masonry and non ductile reinforced concrete (RC) frame construction caused unacceptably high human and economic losses in past earthquakes
This prompted a need for developing and/or promoting alternative building technologies
The goal is to achieve enhanced seismic performance using technologies which require similar (preferably lower) level of construction skills and are economically viable

## Slide 3: Why Confined Masonry in Nepal?
An opportunity for improved seismic performance both for unreinforced masonry and reinforced concrete frame construction in low- and medium-rise buildings

## Slide 4: An Alternative to RC Frame Construction

## Slide 5: An Alternative to Unreinforced Masonry Construction

## Slide 6: Confined Masonry and RC Frame Construction: Performance in Recent Earthquakes
January 2010, Haiti
M 7.0
300,000 deaths
February 2010, Chile
M 8.8 521 deaths
(10 due to confined masonry construction)

## Slide 7: Beginnings
Evolved though an informal process based on its satisfactory performance in past earthquakes
The first reported use in the reconstruction after the 1908 Messina, Italy earthquake (M 7.2) - death toll 70,000
Practiced in Chile and Columbia since 1930’s and in Mexico since 1940’s
Currently practiced in several countries/regions with high seismic risk, including Latin America, Mediterranean Europe, Middle East (Iran), South Asia (Indonesia), and the Far East (China).

## Slide 8: Confined Masonry (CM) Construction)
It consists of masonry walls and horizontal and vertical RC confining members built on all four sides of a masonry wall panel.

## Slide 9
Confined Masonry Construction
Notes: `

## Slide 10: Components of CM
Confined Masonry
Masonry wall
Confining Elements
(RC-Columns & RC-Tie beams
Plinth Band
Floor and Roof
Slabs
Foundation

## Slide 11
Key features
of
Structural Component

## Slide 12: Confining elements (RC tie-columns and RC tie-beams)
Horizontal(tie-beams) & Vertical(tie-columns) RC confining members built in all four side of wall
Provide restraint to masonry walls and protect them from complete disintegration even in major earthquakes
Enhance the stability and integrity of masonry walls for in-plane & out- of- plane earthquake loads.

## Slide 13: Confining elements (RC tie-columns and RC tie-beams)
Enhance the strength(resistance) of masonry wall under lateral earthquake loads
Reduce the brittleness of masonry walls under earthquake hence improving their earthquake performance

## Slide 14: Masonry Wall
Made of solid clay bricks, hollow clay tiles, or concrete blocks
Confined by tie-columns & tie-beams
Transmit the gravity load from the slab(s) above down to the foundation
Act as bracing panels, which resist horizontal earthquake forces

## Slide 15: Floor & roof Slabs
Transmit both gravity & lateral loads to the wall
In Earthquake slab behave lake a horizontal beam & Called diaphragm
Plinth band
Transmit the load from wall to the foundation
Foundation
Transmit the load from the structure to the ground

## Slide 16: Confined Masonry versus Reinforced Masonry
Vertical and horizontal reinforcing bars are provided to enhance the strength and ductility of masonry walls
Reinforcement is concentrated in vertical and horizontal RC confining elements whereas the masonry walls are usually free of reinforcement

## Slide 17
Reinforced Concrete Frame Construction

## Slide 18: Confined Masonry versus Infilled RC frames:
Confined Masonry
  Walls first
  Concrete later
Reinforced Concrete Infilled Frame
  Concrete first
  Walls later
- construction sequence
- integrity between masonry and frame

## Slide 19: Confined Masonry vs RC Frames with Infills – Key Differences

## Slide 20
Seismic Forces vs Confined Masonry wall

## Slide 21: Monolithic action of a masonry wall & RC confining elements

## Slide 22: Mechanism of shear resistance

## Slide 23: Mechanism of shear resistance
Three stages:
Onset of diagonal cracking
Cracking propagated through RC tie-columns
Failure

## Slide 24
Confined Masonry Building : Vertical Truss Model (left) and Collapse at the Ground Floor Level (right)

## Slide 25: Critical Region

## Slide 26: Failure modes of Confined Masonry buildings (not well designed or constructed)
Masonry damage (in- and out-of-plane)
RC tie-columns
Tie-beam-to-tie-column joints
Confining elements around openings

## Slide 27: In-plane shear failure of masonry wall
Earthquake ground shaking in the direction parallel with the longitudinal wall axis

## Slide 28: Out-of-Plane Wall Damage
An example of out-of-plane damage observed in a three-storey building
The damage concentrated at the upper floor levels
The building had concrete floors and timber truss roof
The same building suffered severe in-plane damage
Earthquake ground shaking perpendicular to the longitudinal wall axis

## Slide 29: Out-of-Plane Wall Failure

## Slide 30: Tie-Column Failure

## Slide 31: Buckling of a RC Tie-Column

## Slide 32: Shear Failure of RC Tie-Columns

## Slide 33: Tie-beam-to-tie-column joints
Inadequate anchorage of tie-beam reinforcement

## Slide 34: Tie-beam-to-tie-column joints
Due to Poor reinforcements detailing

## Slide 35: Tie-beam-to-tie-column joints
Absence of of ties in joint Area

## Slide 36: Absence of Confining elements around openings

## Slide 37: In-Plane Shear Cracking – the Effect of Confinement
Unconfined openings | Confined openings

## Slide 38: Key Causes of Damages
Inadequate wall density
Poor quality of masonry materials and construction
Inadequate detailing of reinforcement in confining elements
Absence of confining elements at openings

## Slide 39: Construction Guideline for CM Construction
Architectural Guideline
Construction Guideline
Non-engineered Building
(Inspection form is for One storey only)

## Slide 40
Architectural Guideline

## Slide 41: Symmetrical wall
Inadequate plan : layout
Adequate shape

X

## Slide 42: Regular Building Plan
Irregular
Symmetrical

X

## Slide 43: Plan Shape : Length-to-width ratio less than 3 times
Poorly proportioned plan
Well proportioned plan

X

## Slide 44: Walls should be continuous up the building height
Load path not clear
Load path clear

X
Wall height: 3m for Non-Designed Building.

## Slide 45: Opening
Poor Location of Window and door opening
Good location of window and door
opening

X
Opening Should be placed in the same same position up the building height

## Slide 46: Location of Confining Elements
Vertical Spacing of tie- beam should not exceed 3m & Should be at every floor
Tie-columns should be placed at a maximum spacing of less than 4.5 at wall to wall intersections , free end of wall & within wall if its lengths exceed than MRS

## Slide 47: Wall Distribution
Inadequate Wall Distribution
Adequate Wall Distribution

X
At least three fully confined walls should be provided in each direction

## Slide 48
Walls Density
Eurocode 8 (1996)
At least 2% for a site with a design ground accln up to 0.2g (corresponding to seismic zone II of India
At least 4% for a site with a design ground accln up to 0.3g (corresponding to seismic zone III of India
At least 5% for a site with a design ground accln up to 0.4g (corresponding to seismic zone IV of India
At least 5 % in each of two orthogonal direction

## Slide 49
Construction Guideline

## Slide 50: Wall (Constructing method)
Toothing enhances interaction between masonry walls and RC confining elements
Wall thickness: 230 mm

## Slide 51: Tie -Column
Tie-column reinforcement set in the position prior to the Construction of Foundation and wall
Should be Place at wall ends, intersection & Opening

## Slide 52: Tie –Column (Reinforcements)
Tie Column Size : (230 X 230 )mm at Corner & wall Section
230 X 115) mm at Opening
Longitudinal reinforcements: 4  12mm bar at corner & wall section
2  12mm bars at Opening
Stirrups: 6 mm @ 150 c/c

## Slide 53: Tie-beam
Horizontal ties Size : (230 X 150 )mm
Longitudinal reinforcements: 4  12mm bar at corner & wall section
Stirrups: 6 mm @ 150 c/c
Team-Beam are constructed atop the wall of each floor level

## Slide 54: Tie-beam
Horizontal Size : (230 X 150 )mm
Longitudinal reinforcements: 4  12mm bar at corner & wall section
Stirrups: 6 mm @ 150 c/c

## Slide 55: Joint Detailing


It is preferred to place beam reinforcement outside the column reinforcement cage

## Slide 56: Foundation and Plinth Construction
Similar as traditional masonry construction
Minimum foundation depth & width 900 mm

## Slide 57: Slab
Should be on uniform level
Minimum thickness: 125 mm
Reinforcement: 8mm bar @ 150mm c/c
Minimum Cover: 15 mm

## Slide 58: Construction Process

## Slide 59
Confined Masonry Construction
Notes: `

## Slide 60
Thank You !